## Sheet1
| Tier 1 | Tier II | Tier III | Tier IV
Building Type | Tenant | Tenant | Stand-alone | Stand-alone
Staffing | None | 1 Shift | 1 + Shifts | "24 by Forever"
Useable for Critical Load | 100% N | 100% N | 90% N | 90% N
Initial Gross Watts per Square Foot (W/ft2) (typical) | 20-30 | 40-50 | 40-60 | 50-80
Ultimate Gross W/ft2 (typical) | 20-30 | 40-50 | 100-1501,2,3 | 150+1,2
Uninterruptible Cooling | None | None | Maybe | Yes
Support Space to Raised-Floor Ratio | 20% | 30% | 80-90%2 | 100+%
Raised-Floor Height (typical) | 12" | 18" | 30-36"2 | 30-36"2
Floor Loading lbs/ft2 (typical) | 85 | 100 | 150 | 150
Utility voltage (typical) | 208, 480 | 208, 480 | 12-15 kV2 | 12-15 kV2
Single Points-of-Failure | Many + human error | Many + human error | Some + human error | None + human error
Annual Site-Caused IT Downtime (actuals) | 28.8 hours | 22.0 hours | 1.6 hours | 0.4 hours
Site Availability | 99.67% | 99.75% | 99.98% | 100%
Months to Implement | 3 | 3-6 | 15-20 | 15-20
Year First Deployed | 1965 | 1970 | 1985 | 1995
Construction Cost (+30%)1,2,3 Raised Floor Useable UPS Output | $220/ft2 $10,000/kW | $220/ft2 $11,000/kW | $220/ft2 $20,000/kW | $220/ft2 $20,000/kW